Check whether the rpm is normal.

Check all temperatures and pressures of the following:

- Cooling water

- Lubricating oil

- Scavenge air

- Fuel oil

Check all cooler inlet/outlet temperatures of both the cooling medium and the medium being cooled.

This includes the following:

- Scavenge cooler

- Lubricating oil cooler

- Jacket water cooler

- Check exhaust temperature of all units as well as inlet and outlet of turbocharger.

- Check all oil levels sump, governor, turbocharger and rocker arm (If provided).

- Check for leaks in air, lubricating oil, cooling water and exhaust systems.

- Check for abnormal noise and vibrations.

- Check for rated voltage and frequency from the control room.

- Check the power.

- Continue the above checks for 5 to 10 minutes. If there are no abnormalities the generator is taken on load.

- Once on load, periodic monitoring of the above parameters is essential to avert any disaster.

The normal operating values are:

Exhaust gas temperature 300°C to 400°C

Cooling water temperature 75° to 80°C, 2.8 kg/cm2

Lubricating oil temperature 45°C, 3.5 kg/cm2

Fuel oil temperature 105°C to 130°C (Viscosity 13 cSt)

The normal values for the turbocharger unit are:

Exhaust gas temperature at inlet and outlet 450/250°C

Air temperature at inlet and outlet 35/129°C